## Slide 1: Decoded 2 – Fire Door Assemblies
Audio Dial-In: 866-430-4132
Audio Code: 781-453-5306
Mute your phone (*6 to mute, #6 to unmute).
This webinar is being recorded.

## Slide 2: Session 2 – Fire Doors
NFPA 80 – format and organization
Purpose of fire doors
Fire ratings and testing
Basic fire door requirements
Fire Door Assembly Inspection

## Slide 3: NFPA 80
NFPA 80 details the requirements for fire doors.
NFPA 80 does not state where fire doors are required.
Referenced by the IBC, NFPA 101, and other codes.
Recent Editions: 1999, 2007, 2010, 2013
COR140 exam uses the 2007 edition

## Slide 4: NFPA 80
Does anyone know what the * or the | indicate?
Type in the chat box.
?

## Slide 5: NFPA 80
* = More information in Annex A – Explanatory Material
| = Revised in the last code change cycle.

## Slide 6: NFPA 80
Chapter 1 – Administration
Chapter 2 – Referenced Publications
Chapter 3 – Definitions
Chapter 4 – General Requirements
Chapter 5 – Care and Maintenance
Chapter 6 – Swinging Doors with Builders Hardware
Chapter 7 – Swinging Doors with Fire Door Hardware
Chapters 8-20 – Other Types of Doors, Glass Block, Dampers, Curtains
Annexes
P06

## Slide 7
Swinging Doors with Builders Hardware

## Slide 8
Swinging and Sliding Doors with Fire Door Hardware

## Slide 9: Classification of Openings
Class A—Openings in fire walls and in walls that divide a single building into fire areas
Class B—Openings in enclosures of vertical communications through buildings and in 2-hour rated partitions providing horizontal fire separations
Class C —Openings in walls or partitions between rooms and corridors having a fire resistance rating of 1 hour or less
Class D—Openings in exterior walls subject to severe fire exposure from outside the building
Class E—Openings in exterior walls subject to moderate or light fire exposure from outside the building

## Slide 10: Fire Door Ratings
Most Common
    A – 3 hours
    B – 90 minutes or 60 minutes
    C – 45 minutes
    20 minutes

## Slide 13
What’s the point?

## Slide 14: History has shown us the importance of operational fire and egress doors. A warehouse fire in 1996 left only the part of the building protected by fire doors intact. Source: NFPA Journal

## Slide 15: The Robert Moses Nature Center was protected by this fire door.
Photos: Paul Martin

## Slide 21
Notes: Watch this video on class page later.

## Slide 22: Fire doors must be closed and latched at the time of a fire.
thumb

## Slide 23: Operation of Doors
Self-Closing = standard door closer without a hold-open mechanism
Automatic-Closing = door closer with electric or battery-operated hold-open mechanism actuated by the fire protection system or a smoke detector
Power-Operated Fire Doors = door with an automatic operator – must be deactivated upon fire alarm

## Slide 24: Question
Can you think of any locations where a fire door is not required to be self-closing?
Type in the chat box.

## Slide 25: Exception
Fire doors in common walls between R-1 sleeping units
AKA communicating doors between hotel rooms

## Slide 26: Exception
Inactive leaf of rated pair to unoccupied room
  Boiler room
  Electric room
  Mechanical room

## Slide 27: Acceptable Ways to Hold Open a Fire Door
Non-detectored electronic hold-open unit released by fire alarm.
Electronic hold-open unit with on-board detector.

## Slide 28: Not OK

## Slide 29: Not OK

## Slide 30: Not OK

## Slide 31: Fusible Link Arms

## Slide 32: Fusible Link Arm
Current codes require smoke-actuated hold-opens for almost all fire door locations.

## Slide 33: Acceptable Ways to Hold Open a Fire Door
wall or floor magnet with closer

## Slide 34: Not OK

## Slide 35: Not OK

## Slide 36: OK?

## Slide 37: Acceptable Ways to Hold Open a Fire Door
electro-magnetic hold-open closer

## Slide 38: Anyone know what products were used here?

## Slide 39: Anyone know what products were used here?

## Slide 40: 4111-Cush x 4040-SEH

## Slide 41: Acceptable Ways to Hold Open a Fire Door
battery-operated detectored holder with closer
GJ Sensaguard 280

## Slide 42: Stair Enclosures
“The release by means of smoke detection of one door in a stair enclosure results in closing all doors serving that stair.”

## Slide 43: Self Latching Positive Latching
Must have an active latch bolt

## Slide 44: Not OK

## Slide 45: Latch Throw
NFPA 80 – 2007:
6.4.4.6 Throw.
6.4.4.6.1 The throw of single-point latch bolts shall not be
less than the minimum shown on the fire door label.
6.4.4.6.2 The minimum throw shall be as specified in the
manufacturer’s installation instructions.
In previous editions, a minimum latch throw was spelled out in NFPA 80.

## Slide 46: Self Latching Positive Latching
No Mechanical Dogging

## Slide 47: Self Latching Positive Latching
Latch may be held back electrically (EL/QEL) and release on fire alarm.
No Mechanical Dogging

## Slide 48: Not OK

## Slide 49
Not OK

## Slide 50
Not OK

## Slide 51: Self Latching Positive Latching
Electric Strikes – must be Fail Secure
  Fail Secure – When power fails, keeper is secure
  Fail Safe – When power fails, keeper is free

## Slide 52: Open Back Strikes
NFPA 80 – 2007:
6.4.4.10* Open back strikes shall be permitted to be used in lieu of conventional strikes only where specifically provided
for in the published listings.

## Slide 53: Self Latching Positive Latching
Automatic Flush Bolts
  No “Dummy” Trim on Egress Side
  Coordinator Required

## Slide 54: Flush Bolts
manual
automatic

## Slide 55: Door Coordinators
Pairs of doors
Used with automatic flush bolts and astragals
Coordinates closing of doors so the correct door closes first
Bar type and gravity type
  Bar type installs under frame head
  Gravity type installs on frame face

## Slide 56: Door Coordinators
Pairs of doors with automatic flush bolts or astragals
Coordinates closing of doors so correct door closes first
Bar type and gravity type
  Bar type installs under frame head
  Gravity type installs on frame face

## Slide 58: Door Coordinator
inactive active

## Slide 59: Door Coordinator
inactive active

## Slide 60: Door Coordinator
inactive active

## Slide 61: Door Coordinators

## Slide 62: Door Coordinator
inactive active

## Slide 63: Door Coordinator
inactive active

## Slide 64: Door Coordinator
inactive active

## Slide 65: Door Coordinator
inactive active

## Slide 66: Door Coordinator
inactive active

## Slide 67: Uncoordinated

## Slide 68: Astragals
NFPA 80 – 2007:
6.4.7* Astragals.
6.4.7.1 Doors swinging in pairs, where located within a means of egress, shall not be equipped with astragals that inhibit the free use of either leaf.
6.4.7.2* Pairs of doors that require astragals shall have at least one attached in place to project approximately 3⁄4 in. (19 mm) or as otherwise indicated in the individual published listings.
Previous editions of NFPA 80 required astragals for doors rated more than 90 minutes.

## Slide 69: The overlapping astragal on this pair will prevent one door from being opened.

## Slide 70: Fire Test Methods

## Slide 71
-0.1 0.0 0.1
1/3
2/3
-0.1 0.0 0.1
Early Stage

## Slide 72
-0.1 0.0 0.1
1/3
2/
-0.1 0.0 0.1
Advanced Stage

## Slide 73: In Real Life
The level of thermal discontinuity can be clearly seen here.
The neutral pressure plane would be just above that level.
Notes: 7

## Slide 74: Fire Test Methods
UL 10B – Neutral/Negative Pressure
  Neutral pressure plane at top of the tested assembly
UL 10C – Positive Pressure
  Neutral pressure plane at 40” above the floor
NFPA 252 - Flexible - May be conducted using positive pressure (at 40” above the floor), or neutral pressure (@ top of door)
Category A Doors – intumescent is part of door (if required)
Category B Doors – intumescent is field-applied (if required)
P73

## Slide 75: Fire Test Methods
IBC 2009:
715.4.1 Side-hinged or pivoted swinging doors. Fire door assemblies with side-hinged and pivoted swinging doors shall be tested in accordance with NFPA 252 or UL 10C.
After 5 minutes into the NFPA 252 test, the neutral pressure level in the furnace shall be established at 40 inches (1016 mm) or less above the sill.
NFPA 101 2009 allows either method of fire testing.

## Slide 76: Gasketing
Some fire doors must be tested in accordance with UL1784 for air infiltration
The maximum air leakage rate of the door assembly shall be 3.0 ft3/min/ft2 of door opening...
Gasketing is required to limit air infiltration to this maximum.
Gasketing must be listed for use on fire doors.
A bottom seal is not required for fire doors in most locations.

## Slide 77: Other Fire Door Basics…
Job-Site Preparations

## Slide 78: Acceptable Job Site Preparations
Function holes for mortise locks
Holes for labeled viewers
¾” undercutting on wood and composite doors
Surface-applied hardware
  Drilling round holes up to 1” maximum diameter
  Fasteners
  Cylinders (may be larger than 1” diameter)

## Slide 79: When material is removed, holes must be filled with steel fasteners, or the same material as the door or frame.

## Slide 80: When material is removed, holes must be filled with steel fasteners, or the same material as the door or frame.

## Slide 81: Glazing

## Slide 82: Glazing
Glass in all doors must now be impact-resistant – no exception for fire doors.

## Slide 83: Clearance
Bottom of Door
  3/4” max under the door
  3/8” max if bottom of door is more than 38” a.f.f.
Jambs, Head, and Meeting Stiles
  Hollow Metal Doors – 1/8” +/- 1/16”
  Wood Doors – 1/8”

## Slide 85: Panic hardware for fire doors is Fire Exit Hardware
Label: “Fire door to be equipped with fire exit hardware.”
No mechanical dogging
Less bottom rod applications
  “Fire pins” are used to fix door panels in the closed position.
  Hardware is not required to be operable after fire

## Slide 86: What’s wrong here? Type in the chat box.

## Slide 88: Protection Plates
16” maximum above the bottom of the door
Or UL listed
Or installed “under label service”

## Slide 89: Hinges for Fire Doors
Steel base material
Ball bearing
Proper size, weight, and quantity
2 hinges for 60” in height, 1 additional hinge for each additional 30” (or portion)
Spring hinges are limited to 3070 doors or as tested

## Slide 90: Hinge Fasteners
NFPA 80 – 2007:
6.4.3.2.3 Mortise hinges shall be secured to wood and
plastic-covered composite doors or wood core doors with
No. 12 × 11⁄4 in. (31.75 mm) flat, threaded-to-the-head, steel wood screws. Pilot holes shall be drilled that are 5⁄32 in. (4 mm) in diameter.
6.4.3.2.4 Surface hinges shall be attached with steel throughbolts.
6.4.3.4 Shimming. When required to meet the clearances
stated in 6.3.1.7, the shimming of hinges using steel shims
shall be permitted.

## Slide 91: Not OK

## Slide 92: Signage
NFPA 80 – 2007:
4.1.4 Signage. Informational signs shall be permitted to be installed on the surfaces of fire doors in accordance with 4.1.4.1 through 4.1.4.4 or in accordance with the manufacturer’s published listing.
4.1.4.1 The total area of all attached signs shall not exceed 5 percent of the area of the face of the fire door to which they are attached.

## Slide 93: What’s wrong with this sign? Type in the chat box.

## Slide 94: Screws are not allowed for signage on a fire door.

## Slide 95: Signage
NFPA 80 – 2007:
4.1.4.2 Means of Attachment.
4.1.4.2.1 Signs shall be attached to fire doors by use of an adhesive.
4.1.4.2.2 Mechanical attachments such as screws or nails shall not be permitted.
4.1.4.3 Signs shall not be installed on glazing material in fire doors.
4.1.4.4 Signs shall not be installed on the surface of fire doors so as to impair or otherwise interfere with the proper operation of the fire door.

## Slide 96: Fire Door Assembly Inspection
Added to NFPA 80 in 2007
Responsibility of building owner/property manager
Documents the condition of the fire door assemblies
Fire doors have always been required to be kept in code-compliant condition.

## Slide 97: NFPA 80 Chapter 5
Visual inspection – both sides of door
Functional testing of fire door assemblies
    Ensure door leaves will be closed and latched under fire conditions
Performed by individuals with knowledge and understanding of the operating components of the type of door being subject to testing
Inspection includes operational test of automatic-closing doors
11 inspection criteria in 2007 edition, 13 in 2013 edition
Deficiencies must be repaired “without delay.”

## Slide 98: FDAI Criteria
Label visible and legible
No open holes or breaks in door or frame
Glazing, lite kits, glazing beads securely fastened
Door, frame, hinges, hardware, threshold, secure, aligned, in working order, no damage
No missing or broken parts
Clearances within acceptable limits
Closer functional, door closes completely
Coordinator (if installed) works properly
Latching hardware operates and secures door in closed position
No auxiliary items that inhibit proper operation
No field modifications outside of what is allowed by NFPA 80
Perimeter and meeting stile gasket present if required
Signage meets requirements of NFPA 80

## Slide 99: Session 2 – Fire Doors
NFPA 80 – format and organization
    * asterisk, | vertical line, Chapter 6
Purpose of fire doors
    compartmentalization to protect egress
Fire ratings and testing
    neutral vs. positive pressure
Basic fire door requirements
    closing, latching, hinges, plates, glass, gasketing, clearances, job-site preparation
Fire Door Assembly Inspection

## Slide 100: Homework
Watch the video analysis of 30 Dowling Circle fire.
Apartment building
Doors equipped with spring hinges
Carpet and door sweep prevented doors from closing
1 Firefighter fatality