## Sheet1
| 2015 International Building Code |  | 2015 NFPA 101 - The Life Safety Code
| Delayed Egress | Controlled Egress | Delayed Egress | Controlled Egress
Code Section | 1010.1.9.7 - Delayed Egress | 1010.1.9.6 Controlled egress doors in Groups I-1 and I-2 | 7.2.1.6.1 - Delayed Egress Locking Systems | 18.2.2.2.5 (New Health Care) 19.2.2.2.5 (Existing Health Care) Also refer to 20.1.3.6 (New Ambulatory Health Care) and 21.1.3.6 (Existing Ambulatory Health Care)
Use Groups Where Application is Allowed | Any Use Group except Assembly, Educational, or High Hazard | Only allowed in Use Groups I-1 (alcohol and drug centers, assisted living facilities, congregate care facilities, group homes, halfway houses, residential board and care facilities, social rehabilitation facilities) and I-2 (foster care facilities, detoxification facilities, hospitals, nursing homes, psychiatric hospitals) - where the clinical needs of persons receiving care require their containment (examples in the IBC Commentary include psychiatric areas, dementia units, Alzheimer’s units, maternity units, newborn nurseries, and possibly emergency departments or pediatric areas depending on AHJ preference). Prior to the 2015 edition, this section was limited to Use Group I-2. | Doors serving low- and ordinary-hazard contents in the following new and existing occupancies: Assembly - permitted except on main entrance/exit doors; exception: in airport terminals, delayed egress locks are not permitted on doors in the egress path from the aircraft through the airport loading walkway into the airport terminal building Educational, Day-Care, Health Care, Ambulatory Health Care, Hotels and Dormitories, Apartment Buildings, Mercantile, Business, Industrial, Storage - permitted with no restrictions Lodging or Rooming Houses - limited to one delayed egress device per escape path Residential Board and Care - limited to exterior doors only | New and Existing Health Care Occupancies - where patient special needs require specialized protective measures for their safety (examples in Annex A include pediatric units, maternity units, and emergency departments), all of the requirements below must be met including automatic release. Where the clinical needs of patients require specialized security measures (examples in Annex A include psychiatric, Alzheimer's and dementia units where patients are housed in specialized units) or where patients pose a security threat (examples in Annex A include forensic and detention units), staff must be able to readily unlock doors at all times, but automatic release is not required. Also refer to 20.1.3.6 (New Ambulatory Health Care) and 21.1.3.6 (Existing Ambulatory Health Care).
Required Fire Protection System | Equipped throughout with an automatic sprinkler system or approved automatic smoke or heat detection system. | Equipped throughout with an automatic sprinkler system or approved automatic smoke or heat detection system. | Protected throughout by an automatic fire detection system or an automatic sprinkler system. | Protected throughout with a supervised automatic sprinkler system, AND 1 of the following: a) complete smoke detection system throughout the locked space, OR b) ability to remotely unlock doors from an approved location within the locked space that is constantly attended.
Actuation Time | Up to 3 seconds (was 1 second prior to the 2015 IBC) when force of 15 pounds is applied. | Release is not required to be actuated by an occupant attempting to operate the door. | Up to 3 seconds when a force of 15 pounds is applied. | Release is not required to be actuated by an occupant attempting to operate the door.
Automatic Release Delay | 15-second delay before lock releases to allow egress (30 seconds with AHJ approval). | Lock is not required to release automatically after actuating the door hardware. | 15-second delay before lock releases to allow egress (30 seconds with AHJ approval). | Lock is not required to release automatically after actuating the door hardware.
Rearming After Actuation | Manual rearm required. | Not addressed in the 2015 IBC. | Manual rearm required. | Not addressed by NFPA 101-2015.
Audible Alarm | Audible alarm required. | No audible alarm required. | Audible alarm required. | No audible alarm required.
Signage | Required Signage: "Push [pull] until alarm sounds. Door can be opened in 15 [30] seconds." Signage must be on the door above and within 12 inches of the door exit hardware. New in 2015: Signage must comply with A117.1 requirements. In Group I occupancies, AHJ may allow signage to be omitted for certain types of treatment areas. | No signage required. | Required Signage: "Push [pull] until alarm sounds. Door can be opened in 15 [30] seconds." Signage must be readily visible, durable, with letters not less than 1-inch high and 1/8-inch stroke with a contrasting background, located on the door adjacent to the release device on the egress side. | No signage required.
Action on Actuation of Fire Alarm / Sprinkler System | Unlock for immediate egress (no delay). | Unlock for immediate egress (not required for psychiatric treatment areas where restraint or containment is required because of patients' clinical needs, and - new in 2015 - not required when a listed child abduction system is used in an I-2 hospital nursery or obstetric area). | Unlock (no delay) in the direction of egress upon actuation of sprinkler system, or not more than one heat detector, or not more than two smoke detectors. | Unlock for immediate egress upon activation of the smoke detection system, waterflow in the automatic sprinkler system (not required where patients require specialized security measures or where patients pose a security threat).
Action on Power Failure | Unlock for immediate egress (no delay). | Unlock for immediate egress (not required for psychiatric treatment areas where restraint or containment is required because of patients' clinical needs, and - new in 2015 - not required when a listed child abduction system is used in an I-2 hospital nursery or obstetric area). | Unlock for immediate egress (no delay). | Unlock for immediate egress (not required where patients require specialized security measures or where patients pose a security threat).
Remote Release | Capable of being deactivated at the fire command center and other approved locations. | Capable of being unlocked by a switch which directly breaks power to the lock, located at the fire command center, nursing station, or other approved location (not required for psychiatric treatment areas where restraint or containment is required because of patients' clinical needs, and - new in 2015 - not required when a listed child abduction system is used in an I-2 hospital nursery or obstetric area). | Not addressed in NFPA 101-2015. | Remote control of locks is one option for rapid removal of occupants (see below for additional options). For new occupancies, remote control must be from within the locked area.
Staff Release | Not required. | Procedures for unlocking doors must be part of emergency plan. All clinical staff must carry keys, codes, or other credentials to unlock doors. | Not required. | Staff can readily unlock doors at all times. Rapid removal of occupants facilitated by a) remote control of locks (for new occupancies remote control must be from within the locked area), b) keys carried by staff at all times, or c) other reliable means always available to staff.
Emergency Lighting | Required on the egress side of the door. | Must be provided at the door. | Required on the egress side of the door. | No requirement for emergency lighting referenced in this section.
Maximum Quantity of Devices | One delayed egress lock per egress path. New in 2015: I-2 or I-3 occupancies may have 2 doors with delayed egress locks in one egress path, with a maximum combined delay of 30 seconds. | Occupant must not be required to pass through more than one controlled egress lock before entering an exit (not limited for psychiatric treatment areas where restraint or containment is required because of patients' clinical needs, and - new in 2015 - not limited when a listed child abduction system is used in an I-2 hospital nursery or obstetric area). | Refer to occupancy chapter limitations above. | One locking device per door, maximum, for new occupancies. AHJ may approve more than one lock per door for existing occupancies.
Required Listings for Locking System | UL 294 - Standard for Access Control System Units | UL 294 - Standard for Access Control System Units | No specific listing referenced in this section. | No specific listing referenced in this section.
Type of Locking Hardware Typically Used | Approved, listed, delayed egress panic hardware or fire exit hardware, delayed egress mag-lock, or other electrified lock with listed delayed egress controller. | Controlled egress panic hardware or fire exit hardware, electromagnetic lock, or other fail safe electrified lock. | Approved, listed, delayed egress panic hardware or fire exit hardware, delayed egress mag-lock, or other electrified lock with listed delayed egress controller. | Controlled egress panic hardware or fire exit hardware, electromagnetic lock, or other fail safe electrified lock. Note: NFPA 101-2015 allows these doors to be disguised with murals in existing health care occupancies if certain criteria are met. Refer to section 19.2.2.2.7.
.